## LM
PMC | : PT FEEDBACK INFRA
PROJECT : ASSAM INTRA STATE TRANSMISSION SYSTEM ENHANCEMENT PROJECT
CLIENT : ASSAM ELECTRICITY GRID CORPORATION LIMITED
Observations on: |  |  | Comments on Design & Drawings for 40M hight Lightning Mast for 220kV GIS JAKHALABANDHA SS_ pkg A
Submission Date : 24.04.2023
Sl No. | Drawing / Document No. | Rev. No. | Reference | General Observations | Satcon's Reply Dated 08.05.23
1 | NECCON/AEGCL/PKGA/JAK/C/CAL/098C & NECCON/AEGCL/PKGA/JAK/S/GAD/096 | R0 |  | Provide plstower model member design table for this lattice structure ( Excel sheet) by considering staadpro analysis forces. | As per Technical Specification, no such Softwares to be used for design calulation for steel structures was mentioned, whereas we have designed 40m LM Structure through reputed American Software Bentley StaadPro, whose design calculation is acceptable worldwide. Thus, it is suggested to please accept the Calculation Analysis done by Staad Software.
2 |  | R0 | refer page no.25 to 37 | Some of the member shown in the utilization ratio shows more 90% for the beam no.121,122,126,127,188,189.198,199,870,873,874. | Members were checked and found that utilization ratio of members are less than 90% and revised design calculation with Staad File has been submitted for ready reference.